GTI EL5 CONTROL

GTI EL5 CONTROL is a multi-layered looselay vinyl tile, 6 mm thick, reinforced with 2 glass fibre grids

GTI EL5 CONTROL is available in square format with welded joints for clean environments and watertight systems requirements.

GTI EL5 CONTROL wearlayer is 2 mm vinyl homogeneous manufactured with continuous high pressure process, abrasion group P.

It complies with EN 649 and offers an outstanding resistance to traffic.

This floorcovering is treated with Evercare™ technology: the latest improvements in polyurethane surface treatment obtained by UV laser cross-linking. Evercare™ offers easy maintenance and resistance against staining of chemical products used in healthcare like betadine, eosin or anti-bacterial hand gel; and decontamination protocols.

This treatment has excellent maintenance characteristics; it requires no wax for life!

The carbon encapsulated granules throughout its full thickness and the conductive backing and conductive surface treatment ensure optimal and consistent conductive properties throughout its full life expectancy.

- 5x104 ≤ Rt ≤ 106 according to EN 1081

- Rt ≤ 108 according to CEI 61340-4-1

It has permanent antistatic properties.

- < 2000V according to EN 1815

- < 100V according to CEI 61340-4-5

The product is non-emissive of volatile organic compounds with <10 µg/m3 (TVOC after 28 days ISO 16000-6).

Complementary finishes: GTI EL5 CONTROL ACCESS (access ramp), GTI EL5 CONTROL CORNER (corner finishes), GTI EL5 CONTROL coving (COVING / COVING CORNER IN et COVING CORNER OUT) and conductive welding rods (GTI EL5 CONTROL WELDING RODS).